## Cost Savings
OPERATING COST SAVINGS COMPARISON
GAMATRONIC POWER + THREE-PHASE UPS verses COMPETITOR UPS
| Load Rating (kVA) = | 50
| Load Power Factor = | 0.8
| Load in kW = | 40
| Total Energy Cost per kW/hr = | 0.1
| Internal Rate of Return = | 10%
| Gamatronic Power+ efficiency = | 94%
| Competitor efficiency in double-conversion mode = | 90%
| Energy Loss of Power + (kW) = | 2.4
| Energy Loss of Competitor (kW) = | 4
| Additional energy to operate competitors product (kW) = | 1.6
| Heat Loss of Power + (Btu/hr) = | 8194.56
| Heat Loss of Competitor (Btu/hr) = | 13657.6
| Additional Heat Generated by Competitor (Btu/hr) = | 5463.04
| Daily energy savings using Power + = | 3.84 | Total Amortized Savings
| Yearly energy savings using Power + = | 1401.6
|  |  | # of Years | Savings
| Cooling % efficiency = | 100% | I Year | 2803.2
| Daily cooling savings using Power + = | 3.84 | 2 Years | 5886.72
| Yearly cooling savings using Power + = | 1401.6 | 3 Years | 9278.592
|  |  | 4 Years | 13009.6512
|  |  | 5 Years | 17113.8163
| Total Annual Savings = | 2803.2 | 10 Years | 44675.7886
230 Yuma Street, Denver, CO 80223 ● 800.576.3966 ● www.maxpowercorp.com

## Instructions
Data to be Entered | Notes
Load Rating (kVA) | Enter the total kVA of the load or the output KVA rating of the UPS
Load Power Factor | Enter the Power Factor of the load or the output power factor rating of the UPS. Typical values are .80 - .90.
Total Energy Cost per kW/hr | Enter the Energy (Electricity) cost for your area in cents per kilowatt-hour. See 2007-2008 Energy Cost Worksheet for average prices by State and End User Sector. Add any local taxes or surcharges that are applicable.
Internal Rate of Return | Enter the ROI or cost of money for the company purchasing the UPS. The can be as simple as the interest rate to borrow the money, the return when investing the same money elsewhere or can reflect an established internal rate in %.
Competitor efficiency in double-conversion mode | Enter the Efficiency of the competitive product in %. These values can usually be found on the product literature. In cases of product with "High Efficiency" or "Economy" Modes, The UPS will be operating in bypass rather than double-conversion or UPS mode. The double-conversion efficiency may or may not be stated. If it is not, use 90%.
Cooling % efficiency | Enter the Efficiency of the facilities data center cooling system in %. These values will vary with the type and age of the cooling system. Typical values range from 85 - 100%.

## 2007 - 2007 Energy Cost
Source: Energy Information Administration, Form EIA-826, "Monthly Electric Sales and Revenue Report with State Distributions Report."
Table 5.6.B. Average Retail Price of Electricity to Ultimate Customers by End-Use Sector, by State, Year-to-Date through December 2008 and 2007 (Cents per Kilowatthour)
| Residential |  | Commercial1 |  | Industrial1 |  | Transportation[1] |  | All Sectors
Census Division
and State
| 2008 | 2007 | 2008 | 2007 | 2008 | 2007 | 2008 | 2007 | 2008 | 2007
New England | 17.57 | 16.7 | 15.48 | 14.71 | 13.27 | 12.74 | 11.66 | 10.87 | 15.84 | 15.08
Connecticut | 19.36 | 19.11 | 15.93 | 15.39 | 13.9 | 12.92 | 15.46 | 14.18 | 16.95 | 16.45
Maine | 15.96 | 16.52 | 12.95 | 12.94 | 11.8 | 14.11 | -- | -- | 13.71 | 14.59
Massachusetts | 17.5 | 16.23 | 16.05 | 15.2 | 14.21 | 13.03 | 9.65 | 9.24 | 16.22 | 15.16
New Hampshire | 15.69 | 14.88 | 14.28 | 13.91 | 13.17 | 12.27 | -- | -- | 14.64 | 13.98
Rhode Island | 17.57 | 14.05 | 15.49 | 12.67 | 14.22 | 12.04 | -- | -- | 16.13 | 13.12
Vermont | 14.62 | 14.15 | 12.51 | 12.29 | 9 | 8.92 | -- | -- | 12.32 | 12.04
Middle Atlantic | 15.15 | 13.95 | 14.01 | 13.22 | 8.72 | 7.78 | 12.46 | 10.35 | 13.38 | 12.31
New Jersey | 15.95 | 14.14 | 14.72 | 12.99 | 12.42 | 10.08 | 16.26 | 11.14 | 14.91 | 13.01
New York | 18.79 | 17.1 | 16.45 | 15.92 | 11.97 | 8.71 | 13.5 | 10.96 | 16.74 | 15.22
Pennsylvania | 11.39 | 10.95 | 9.42 | 9.2 | 7.02 | 6.87 | 7.64 | 7.72 | 9.35 | 9.08
East North Central | 10.46 | 9.74 | 8.87 | 8.49 | 6.42 | 5.9 | 7.87 | 6.84 | 8.59 | 7.97
Illinois | 11.07 | 10.12 | 8.53 | 8.57 | 7.83 | 6.61 | 7.52 | 6.43 | 9.21 | 8.46
Indiana | 8.93 | 8.26 | 7.81 | 7.29 | 5.51 | 4.89 | 9.6 | 10.09 | 7.13 | 6.5
Michigan | 10.94 | 10.21 | 9.43 | 8.77 | 6.86 | 6.47 | 11.83 | 9.76 | 9.14 | 8.53
Ohio | 10.13 | 9.57 | 9.26 | 8.67 | 6.23 | 5.76 | 10.68 | 9.98 | 8.44 | 7.91
Wisconsin | 11.6 | 10.87 | 9.28 | 8.71 | 6.54 | 6.16 | -- | -- | 9.04 | 8.48
West North Central | 8.73 | 8.31 | 7.13 | 6.79 | 5.35 | 5.08 | 6.67 | 7.25 | 7.17 | 6.83
Iowa | 9.72 | 9.45 | 7.28 | 7.11 | 4.86 | 4.74 | -- | -- | 7 | 6.83
Kansas | 8.98 | 8.19 | 7.55 | 6.83 | NM | 5.13 | -- | -- | 7.59 | 6.84
Minnesota | 9.79 | 9.18 | 7.86 | 7.48 | 5.96 | 5.69 | 8.04 | 8.27 | 7.83 | 7.44
Missouri | 8.03 | 7.69 | 6.59 | 6.34 | 4.98 | 4.76 | 5.4 | 6.16 | 6.85 | 6.56
Nebraska | 7.82 | 7.59 | 6.64 | 6.39 | 5.05 | 4.78 | -- | -- | 6.51 | 6.28
North Dakota | 7.48 | 7.3 | 6.8 | 6.58 | 5.51 | 5.24 | -- | -- | 6.64 | 6.42
South Dakota | 8.22 | 8.07 | 6.83 | 6.61 | 5.3 | 5.09 | -- | -- | 7.07 | 6.89
South Atlantic | 10.74 | 10.03 | 9.39 | 8.66 | 6.35 | 5.67 | 11.69 | 9.39 | 9.4 | 8.68
Delaware | 13.92 | 13.16 | 12.04 | 11.21 | 10.1 | 8.93 | -- | -- | 12.25 | 11.35
District of Columbia | 12.68 | 11.18 | 13.64 | 12.01 | 11.52 | 9.32 | 15.76 | 11.32 | 13.49 | 11.79
Florida | 11.67 | 11.22 | 10.2 | 9.75 | 8.36 | 7.76 | 10.17 | 9.73 | 10.79 | 10.33
Georgia | 10.06 | 9.1 | 9.19 | 8.07 | 6.76 | 5.53 | 7.15 | 6.42 | 8.96 | 7.86
Maryland | 13.81 | 11.89 | 12.82 | 11.58 | 10.4 | 9.41 | 12.55 | 10.15 | 13.01 | 11.5
North Carolina | 9.72 | 9.4 | 7.67 | 7.43 | 5.62 | 5.47 | 6.57 | 9.09 | 8.12 | 7.83
South Carolina | 9.99 | 9.19 | 8.53 | 7.74 | 5.42 | 4.83 | -- | -- | 7.93 | 7.18
Virginia | 9.7 | 8.74 | 7.38 | 6.38 | 5.84 | 5.07 | 7.8 | 6.73 | 8.06 | 7.12
West Virginia | 7.03 | 6.73 | 6.06 | 5.85 | 4.2 | 3.95 | 6.32 | 6.42 | 5.59 | 5.34
East South Central | 9.27 | 8.35 | 8.98 | 8.07 | 5.72 | 5.04 | 10.17 | 10.31 | 7.82 | 7.01
Alabama | 10.36 | 9.32 | 9.85 | 8.7 | 6.18 | 5.27 | -- | -- | 8.61 | 7.57
Kentucky | 7.97 | 7.34 | 7.25 | 6.76 | 4.81 | 4.47 | -- | -- | 6.25 | 5.84
Mississippi | 10.3 | 9.36 | 9.98 | 8.92 | 6.53 | 5.75 | -- | -- | 8.93 | 8.03
Tennessee | 8.81 | 7.84 | 9.02 | 8.09 | 6.13 | 5.19 | 10.17 | 10.31 | 8.02 | 7.07
West South Central | 11.76 | 11.15 | 10.09 | 9.26 | 8.08 | 7.14 | 8.89 | 8.65 | 10.09 | 9.27
Arkansas | 9.46 | 8.73 | 7.76 | 6.91 | 6.04 | 5.25 | -- | -- | 7.76 | 6.96
Louisiana | 10.39 | 9.37 | 10.1 | 9.13 | 7.87 | 6.77 | 12.26 | 13.91 | 9.38 | 8.39
Oklahoma | 9.25 | 8.58 | 8.04 | 7.33 | 6.01 | 5.41 | -- | -- | 7.97 | 7.29
Texas | 12.83 | 12.34 | 10.65 | 9.87 | 8.8 | 7.79 | 8.64 | 8.4 | 10.93 | 10.11
Mountain | 9.84 | 9.31 | 8.35 | 7.77 | 6.03 | 5.68 | 8.25 | 7.56 | 8.16 | 7.69
Arizona | 10.25 | 9.66 | 8.86 | 8.27 | 6.6 | 6.05 | -- | -- | 9.09 | 8.54
Colorado | 10.15 | 9.25 | 8.56 | 7.62 | 6.65 | 5.97 | 8.32 | 7.18 | 8.62 | 7.76
Idaho | 7.01 | 6.36 | 5.72 | 5.14 | 4.5 | 3.87 | -- | -- | 5.7 | 5.07
Montana | 9.14 | 8.77 | 8.54 | 8.1 | 5.73 | 5.16 | -- | -- | 7.44 | 7.13
Nevada | 11.93 | 11.82 | 10.15 | 10.09 | 7.99 | 8.28 | 9.47 | 9.98 | 9.91 | 9.99
New Mexico | 10.02 | 9.12 | 8.56 | 7.66 | 6.31 | 5.6 | -- | -- | 8.3 | 7.44
Utah | 8.3 | 8.15 | 6.73 | 6.54 | 4.59 | 4.52 | 7.85 | 7.44 | 6.53 | 6.41
Wyoming | 8.18 | 7.75 | 6.7 | 6.25 | 4.51 | 4.1 | -- | -- | 5.68 | 5.29
Pacific Contiguous | 11.94 | 11.82 | 11.45 | 11.19 | 8.03 | 7.89 | 8.15 | 8.33 | 10.88 | 10.71
California | 14.41 | 14.42 | 13.05 | 12.82 | 10.2 | 9.98 | 8.18 | 8.37 | 12.96 | 12.8
Oregon | 8.52 | 8.19 | 7.59 | 7.2 | 4.91 | 5.06 | 6.75 | 6.71 | 7.26 | 7.02
Washington | 7.58 | 7.26 | 6.79 | 6.55 | 5.23 | 4.57 | 5.88 | 5.74 | 6.69 | 6.37
Pacific Noncontiguous | 25.91 | 20.56 | 22.38 | 17.58 | 22.9 | 16.86 | -- | -- | 23.64 | 18.29
Alaska | 16.35 | 15.18 | 13.33 | 12.19 | 14.04 | 12.63 | -- | -- | 14.5 | 13.28
Hawaii | 32.5 | 24.12 | 29.72 | 21.91 | 26.05 | 18.38 | -- | -- | 29.2 | 21.29
U.S. Total | 11.35 | 10.65 | 10.27 | 9.65 | 7.02 | 6.39 | 11.28 | 9.7 | 9.81 | 9.13
[1] See Technical notes for additional information on the Commercial, Industrial, and Transportation sectors.
NM = Not meaningful due to large relative standard error or excessive percentage change.
Notes: • See Glossary for definitions. • Values for 2007 are final. Values for 2008 are preliminary estimates based on a cutoff model sample. See Technical Notes for a discussion of the sample design for the Form EIA-826. Values for January through November 2008 are revised. • Utilities and energy service providers may classify commercial and industrial customers based on either NAICS codes or demands or usage falling within specified limits by rate schedule. • Changes from year to year in consumer counts, sales and revenues, particularly involving the commercial and industrial consumer sectors, may result from respondent implementation of changes in the definitions of consumers, and reclassifications. • Retail sales and net generation may not correspond exactly for a particular month for a variety of reasons (i.e., sales data may include imported electricity). • Net generation is for the calendar month while retail sales and associated revenue accumulate from bills collected for periods of time (28 to 35 days) that vary dependent upon customer class and consumption occurring in and outside the calendar month.
• Totals may not equal sum of components because of independent rounding.
Source: Energy Information Administration, Form EIA-826, "Monthly Electric Sales and Revenue Report with State Distributions Report."